# Greenfield Data Center Development Manual and Ready-to-Build (RTB) Checklist

English version | Project controls, RTB milestones, tenant/client track and buyer data room

# 1. Purpose and definitions

This document is a development checklist and control manual for advancing a greenfield data center site from origination to RTB. Timings are indicative and must be adapted to the jurisdiction, grid-connection queue and project scale.

RTB / Ready-to-Build: The state in which land, power, permits, design, access, fiber, utilities, cost and programme are sufficiently defined and transferable for a buyer to commence construction, subject only to clearly disclosed exceptions.

Tenant: The end user of data center capacity, such as a hyperscaler, enterprise, AI platform or wholesale customer.

Client / buyer: The party acquiring the RTB project or commissioning the project/build-to-suit; it may be an operator, hyperscaler, infrastructure fund or another developer.

# 2. Tenant and client engagement logic

Market sounding can begin once preliminary site control and a credible power path exist. Tenant requirements should influence the project before the Basis of Design is locked. A tenant LOI can enhance sale value, but it is not a universal RTB requirement. The RTB buyer process is normally prepared once grid, permitting and design have reached sufficient maturity.

# 3. RTB milestone gates

| Week | Milestone | RTB mandatory |
| --- | --- | --- |
| 4 | Development strategy approved | Yes |
| 8 | Preferred site under binding control | Yes |
| 8 | Grid application accepted | Yes |
| 24 | Concept masterplan and Basis of Design complete | Yes |
| 28 | Binding grid connection offer obtained | Yes |
| 34 | Grid connection agreement executed | Yes |
| 30 | Planning application validated | Yes |
| 48 | Final planning consent obtained | Yes |
| 56 | Building permit effective | Yes |
| 34 | Diverse fiber solution secured | Yes |
| 48 | Developed design and independent review complete | Yes |
| 56 | Cost and construction programme validated | Yes |
| 56 | Vendor due diligence and data room complete | Yes |
| 60 | RTB sign-off | Yes |

# 4. Detailed development checklist

## Strategy & Development Definition

| ✓ | Activity | Description | Deliverable | RTB | Weeks | Dependencies |
| --- | --- | --- | --- | --- | --- | --- |
| ☐ | Define development and exit strategy | Confirm target product: powered land, powered shell, turnkey/BTS, or build-and-hold; define intended RTB sale point and buyer universe. | Development brief and exit strategy | Yes | 1-3 | None |
| ☐ | Define target capacity and phasing | Set initial IT load, ultimate campus capacity, phase sizes, redundancy level and expansion assumptions. | Capacity and phasing plan | Yes | 1-4 | Development strategy |
| ☐ | Undertake market and customer assessment | Assess demand, competing supply, absorption, pricing, latency needs and customer segments. | Market assessment | No | 1-6 | Development strategy |
| ☐ | Define technical performance envelope | Set target PUE/WUE, availability, density, cooling options, security, sustainability and certification objectives. | Technical requirements brief | Yes | 2-4 | Capacity plan |
| ☐ | Establish project governance | Appoint development lead, legal, planning, power, technical and commercial advisers; establish decision rights and reporting. | Governance matrix | Yes | 1-3 | None |

## Land & Site Control

| ✓ | Activity | Description | Deliverable | RTB | Weeks | Dependencies |
| --- | --- | --- | --- | --- | --- | --- |
| ☐ | Identify and screen candidate sites | Screen for developable area, power proximity, fiber, hazards, access, water, planning compatibility and neighboring uses. | Site screening matrix | Yes | 1-6 | Capacity plan |
| ☐ | Secure exclusivity or option | Negotiate sufficient exclusivity/option period, extension rights, access for surveys, assignability and conditions precedent. | Executed option/exclusivity agreement | Yes | 4-8 | Preferred site |
| ☐ | Complete legal title due diligence | Verify ownership, encumbrances, mortgages, easements, restrictions, rights of way, boundaries and acquisition authority. | Legal title report | Yes | 5-8 | Site control |
| ☐ | Confirm developable footprint | Overlay setbacks, utility corridors, drainage, biodiversity, access and substation areas against required campus layout. | Constraints and developable-area plan | Yes | 5-8 | Surveys |
| ☐ | Complete site surveys | Topographic, boundary, geotechnical, contamination, hydrology/flood, seismic, unexploded ordnance and archaeology as applicable. | Survey reports | Yes | 5-12 | Site access rights |
| ☐ | Secure permanent access and easements | Document road access, construction access, power/fiber corridors, drainage outfalls and third-party easements. | Access and easement agreements | Yes | 10-16 | Concept routes |
| ☐ | Complete land acquisition structure | Agree purchase/lease mechanics, tax treatment, SPV ownership, transferability and closing conditions aligned with permits and grid. | Acquisition agreement in agreed form | Yes | 18-24 | Title DD; option |

## Power & Grid Connection

| ✓ | Activity | Description | Deliverable | RTB | Weeks | Dependencies |
| --- | --- | --- | --- | --- | --- | --- |
| ☐ | Map utility and grid options | Identify transmission/distribution owners, voltage levels, substations, available capacity, queue position and upgrade constraints. | Power options memorandum | Yes | 1-5 | Site shortlist |
| ☐ | Submit formal connection application | Submit load profile, phased capacity, commissioning dates, power quality and redundancy requirements. | Accepted grid application | Yes | 4-8 | Preferred site; capacity plan |
| ☐ | Complete feasibility and impact studies | Undertake load flow, fault level, protection, stability, harmonic and reinforcement studies required by the utility. | Grid study reports | Yes | 8-22 | Grid application |
| ☐ | Obtain binding connection offer | Secure capacity, voltage, point of connection, milestones, costs, securities, long-stop date and energization schedule. | Binding connection offer | Yes | 18-28 | Grid studies |
| ☐ | Execute grid connection agreement | Accept and execute the connection agreement; pay deposits and satisfy initial milestones without creating avoidable termination risk. | Executed connection agreement | Yes | 26-34 | Binding offer |
| ☐ | Develop substation and utility interface design | Define on-site/off-site scope, transformers, switchgear, protection, metering, route, land take and ownership boundaries. | Substation concept and single-line diagram | Yes | 20-34 | Grid studies |
| ☐ | Confirm power delivery schedule and critical path | Integrate utility design, procurement, permits, outages and construction into a credible energization programme. | Utility delivery programme | Yes | 28-36 | Connection agreement |
| ☐ | Define energy procurement and sustainability route | Assess retail supply, PPAs, guarantees of origin, renewable matching, BESS and demand response; document feasible route. | Energy sourcing strategy | No | 24-38 | Load profile; market analysis |
| ☐ | Define emergency generation and fuel strategy | Select generator technology, emissions basis, fuel storage, refill logistics, runtime and permitting assumptions. | Backup power concept | Yes | 20-30 | Technical brief |

## Fiber & Telecommunications

| ✓ | Activity | Description | Deliverable | RTB | Weeks | Dependencies |
| --- | --- | --- | --- | --- | --- | --- |
| ☐ | Map carrier presence and routes | Identify carriers, long-haul routes, metro rings, cable landing connectivity, PoPs, duct availability and known single points of failure. | Carrier and route map | Yes | 3-8 | Site shortlist |
| ☐ | Design physically diverse entry routes | Define at least two independent routes, entries and meet-me-room pathways with no common ducts, bridges or choke points where practicable. | Diverse fiber route plan | Yes | 8-16 | Carrier map; site layout |
| ☐ | Obtain carrier feasibility confirmations | Secure written confirmations covering route, service type, capacity, cost, lead time, dependencies and delivery risk. | Carrier feasibility letters/LOIs | Yes | 12-22 | Route plan |
| ☐ | Secure rights for fiber corridors | Acquire land rights, municipal permits, duct access and wayleaves needed to reach the site boundary and both building entries. | Fiber wayleaves and route rights | Yes | 18-34 | Preferred carrier routes |
| ☐ | Validate latency and network resilience | Test or model latency to required hubs and cloud regions; review route resilience, repair arrangements and carrier diversity. | Connectivity performance report | No | 18-28 | Carrier confirmations |

## Planning, Environmental & Permitting

| ✓ | Activity | Description | Deliverable | RTB | Weeks | Dependencies |
| --- | --- | --- | --- | --- | --- | --- |
| ☐ | Confirm zoning and permitted use | Obtain written planning advice on data center use, building height/massing, generators, substations, cooling plant and future phases. | Planning due-diligence opinion | Yes | 4-10 | Preferred site |
| ☐ | Agree permitting strategy with authorities | Hold pre-application meetings; define required applications, studies, consultations, sequencing and expected decision timetable. | Permitting strategy and authority minutes | Yes | 8-14 | Concept development |
| ☐ | Complete environmental baseline and impact studies | Cover ecology, habitat, noise, air emissions, traffic, water, waste, visual impact, carbon, contamination and cumulative effects. | Environmental technical studies | Yes | 10-28 | Survey access; concept design |
| ☐ | Submit planning/development application | Submit coordinated plans, design statement, EIA where required, utility information, mitigation and construction-management principles. | Validated planning application | Yes | 24-30 | Environmental studies; concept design |
| ☐ | Obtain final planning consent | Secure consent with conditions that are technically and commercially acceptable and capable of discharge before construction. | Final planning consent | Yes | 30-48 | Planning application |
| ☐ | Secure environmental and operating permits | Obtain permits for generators/emissions, fuel storage, water abstraction/discharge, waste, noise and other regulated activities. | Environmental/operating permits | Yes | 28-48 | Environmental studies; technical design |
| ☐ | Obtain building permit / construction authorization | Advance design to the level required for approval; coordinate fire, structural, civil, MEP and code compliance. | Effective building permit | Yes | 40-56 | Planning consent; developed design |
| ☐ | Discharge pre-construction conditions | Close planning and permit conditions required before works, including traffic, ecology, drainage, archaeology and construction management. | Condition discharge approvals | Yes | 46-58 | Planning consent |

## Water, Cooling & Utilities

| ✓ | Activity | Description | Deliverable | RTB | Weeks | Dependencies |
| --- | --- | --- | --- | --- | --- | --- |
| ☐ | Confirm cooling strategy | Select air, evaporative, liquid or hybrid cooling based on climate, density, customer requirements, water availability and permitting. | Cooling strategy | Yes | 10-18 | Technical performance brief |
| ☐ | Confirm water availability and quality | Obtain utility capacity confirmation or alternative supply; assess quality, treatment, redundancy and drought restrictions. | Water supply confirmation | Yes | 10-22 | Cooling strategy |
| ☐ | Develop drainage and flood-management design | Define surface-water attenuation, discharge points, oil interceptors, foul drainage, finished levels and climate resilience. | Drainage and flood strategy | Yes | 14-28 | Topo/hydrology surveys |
| ☐ | Confirm other utilities and services | Verify potable water, sewer, gas if used, telecom ducts, fire-water supply, waste services and temporary construction utilities. | Utility availability schedule | Yes | 12-24 | Site layout |
| ☐ | Assess heat reuse opportunity and obligations | Review regulatory requirements, nearby heat demand, network interface, economics and reservation of space for future connection. | Heat reuse assessment | No | 18-30 | Cooling strategy; planning |

## Technical Design & Engineering

| ✓ | Activity | Description | Deliverable | RTB | Weeks | Dependencies |
| --- | --- | --- | --- | --- | --- | --- |
| ☐ | Prepare masterplan and concept design | Coordinate buildings, phases, setbacks, substations, generators, cooling, fuel, roads, security, drainage, fiber and expansion. | Coordinated concept masterplan | Yes | 10-22 | Site surveys; technical brief |
| ☐ | Prepare Basis of Design | Document design criteria for availability, topology, capacity, redundancy, densities, environmental conditions, codes and commissioning. | Approved Basis of Design | Yes | 14-24 | Technical brief; concept |
| ☐ | Develop civil and structural design | Advance grading, foundations, slabs, roads, retaining structures, drainage, seismic and loading assumptions. | Developed civil/structural package | Yes | 22-42 | Geotech; concept |
| ☐ | Develop electrical design | Define HV/MV/LV topology, transformers, UPS, generators, switchgear, busways, earthing, protection, metering and controls. | Electrical developed design and SLDs | Yes | 22-44 | Grid interface; Basis of Design |
| ☐ | Develop mechanical and cooling design | Define cooling plant, distribution, heat rejection, water systems, controls, leak detection and future high-density capability. | Mechanical developed design | Yes | 22-44 | Cooling strategy; Basis of Design |
| ☐ | Develop fire and life-safety strategy | Coordinate fire compartments, detection, suppression, smoke control, egress, emergency response and fire-brigade access. | Fire strategy and authority submission | Yes | 20-40 | Concept design |
| ☐ | Develop security design | Define perimeter, vehicle control, anti-ram measures, CCTV, access control, security zoning and operational procedures. | Security concept/design | Yes | 24-40 | Masterplan; customer requirements |
| ☐ | Define controls, BMS and DCIM architecture | Set monitoring hierarchy, integration, alarms, cybersecurity, metering, capacity management and customer reporting requirements. | Controls architecture | No | 28-44 | MEP design |
| ☐ | Prepare commissioning strategy | Define levels 1-5, integrated systems testing, load banks, utility interfaces, documentation, witness points and acceptance criteria. | Commissioning plan | Yes | 32-46 | Developed design |
| ☐ | Undertake independent technical review | Have an experienced data center engineer review constructability, redundancy, maintainability, code compliance and cost risks. | Independent design review report | Yes | 40-48 | Developed design |

## Commercial: Tenant, Client & Exit

| ✓ | Activity | Description | Deliverable | RTB | Weeks | Dependencies |
| --- | --- | --- | --- | --- | --- | --- |
| ☐ | Define customer and buyer universes | Separate end users/tenants from RTB buyers such as operators, hyperscalers, infrastructure funds and developers. | Target customer and buyer list | No | 8-14 | Market assessment |
| ☐ | Begin confidential market sounding | Test location, power timing, capacity, specification and commercial appetite without committing the project prematurely. | Market feedback log | No | 14-30 | Credible power path; concept |
| ☐ | Collect tenant technical requirements | Capture density, topology, cooling, network, sustainability, security, deployment timing and contractual requirements. | Customer requirements register | No | 20-38 | Market sounding |
| ☐ | Run tenant/client technical workshops | Validate fit, identify deviations, preserve design flexibility and agree information required for an LOI or capacity reservation. | Workshop minutes and action log | No | 26-44 | Customer requirements |
| ☐ | Negotiate tenant LOI or capacity reservation | Agree capacity, delivery date, indicative pricing, term, security, design assumptions, exclusivity and conditions to definitive lease/BTS agreement. | Tenant LOI/capacity reservation | No | 34-52 | Technical fit; commercial approval |
| ☐ | Prepare RTB sale positioning | Define sale perimeter, transaction structure, buyer diligence package, value narrative, unresolved risks and pricing expectations. | RTB sale strategy | Yes | 42-54 | RTB scope; financial model |
| ☐ | Launch buyer process | Prepare teaser/IM, NDA, process letter, data room, management presentation and controlled Q&A process. | Buyer process materials | No | 52-60 | RTB readiness; sale strategy |

## Cost, Procurement & Delivery Strategy

| ✓ | Activity | Description | Deliverable | RTB | Weeks | Dependencies |
| --- | --- | --- | --- | --- | --- | --- |
| ☐ | Prepare development budget | Capture land, advisers, surveys, permits, grid deposits, design, insurance, financing and contingency through RTB. | RTB development budget | Yes | 4-12 | Development plan |
| ☐ | Prepare class 4/3 capital cost estimate | Estimate enabling works, buildings, MEP, utility connection, long-lead equipment, commissioning, owner costs and contingency by phase. | Phased capital cost estimate | Yes | 30-46 | Developed design |
| ☐ | Define contracting strategy | Select EPC, design-build, construction management or multi-package approach; allocate design, interface, schedule and performance risk. | Contracting strategy memorandum | Yes | 28-42 | Concept design; market capacity |
| ☐ | Prequalify contractors and key suppliers | Assess data center references, financial strength, safety, local delivery capability, capacity, warranty support and supply chain. | Approved bidder/supplier list | Yes | 34-48 | Contracting strategy |
| ☐ | Identify long-lead equipment and reservations | Confirm lead times for transformers, switchgear, generators, UPS, chillers and controls; obtain budget quotes and reservation options. | Long-lead procurement schedule | Yes | 32-48 | Developed design |
| ☐ | Prepare construction and procurement programme | Integrate design, permits, utility works, procurement, enabling works, main construction, commissioning and customer fit-out interfaces. | Integrated delivery programme | Yes | 42-54 | Design; utility programme; procurement |
| ☐ | Obtain credible contractor pricing | Run market testing or tender sufficient to validate cost, schedule, exclusions, escalation and contingency before RTB sale. | Contractor proposals / cost validation | Yes | 44-56 | Developed design; bidder list |

## Financial, Tax, Insurance & Corporate

| ✓ | Activity | Description | Deliverable | RTB | Weeks | Dependencies |
| --- | --- | --- | --- | --- | --- | --- |
| ☐ | Establish project SPV and ownership structure | Create clean project ownership, governance, bank accounts, signing powers, IP/document ownership and transfer mechanics. | Project SPV and governance documents | Yes | 2-8 | Development strategy |
| ☐ | Prepare integrated financial model | Model development spend, capex, phasing, power costs, operating assumptions, rent/revenue, financing and sale scenarios. | Integrated financial model | Yes | 24-44 | Cost estimate; commercial assumptions |
| ☐ | Complete tax and transaction structuring | Assess land taxes, VAT, depreciation, withholding, transfer taxes, share vs asset sale and buyer implications. | Tax structuring memorandum | Yes | 30-44 | SPV; sale strategy |
| ☐ | Define insurance strategy | Identify development, property, environmental, professional indemnity, construction, delay and operational coverage requirements. | Insurance strategy and broker indication | No | 34-48 | Risk register; design |
| ☐ | Fund development through RTB | Secure committed equity/loan funding sufficient for land, studies, grid securities, permits, design and sale process with contingency. | Funding plan and evidence of funds | Yes | 6-18 | Development budget |

## Risk, ESG, HSE & Stakeholders

| ✓ | Activity | Description | Deliverable | RTB | Weeks | Dependencies |
| --- | --- | --- | --- | --- | --- | --- |
| ☐ | Maintain integrated risk register | Track probability, impact, mitigation, owner, trigger and residual exposure across land, power, permits, cost, schedule and commercial workstreams. | Current risk register | Yes | 2-60 | All workstreams |
| ☐ | Prepare stakeholder engagement plan | Map authorities, utility, neighbors, community, carriers, emergency services and political stakeholders; define engagement and escalation. | Stakeholder plan | Yes | 6-14 | Site selection |
| ☐ | Define ESG and sustainability commitments | Set measurable targets for energy, carbon, water, biodiversity, circularity, local employment and reporting without overcommitting. | ESG strategy | No | 12-26 | Technical and market strategy |
| ☐ | Prepare construction HSE framework | Define client duties, contractor standards, high-risk activities, emergency arrangements, reporting and preconstruction information. | HSE management framework | Yes | 40-54 | Delivery strategy |
| ☐ | Assess climate and physical resilience | Review heat, flood, drought, wildfire, storm, seismic and supply-chain exposure under current and future climate scenarios. | Climate resilience assessment | Yes | 12-26 | Environmental baseline; design criteria |

## RTB Transaction & Data Room

| ✓ | Activity | Description | Deliverable | RTB | Weeks | Dependencies |
| --- | --- | --- | --- | --- | --- | --- |
| ☐ | Define formal RTB completion standard | Agree a written RTB definition covering land, power, planning, building permit, design, access, fiber, utilities, cost, programme and assignability. | RTB completion checklist | Yes | 36-44 | Exit strategy; buyer feedback |
| ☐ | Build indexed virtual data room | Create controlled folders for corporate, land, power, permits, environment, design, fiber, utilities, commercial, cost, programme, insurance and tax. | Indexed virtual data room | Yes | 36-56 | Document control system |
| ☐ | Complete vendor legal due diligence | Identify title, authority, contract, permit, litigation, compliance and transfer risks; cure issues before buyer review. | Vendor legal DD report | Yes | 46-56 | Substantially complete data room |
| ☐ | Complete vendor technical due diligence | Independently validate site suitability, power, design, permits, capex, schedule, fiber, utilities, ESG and key residual risks. | Vendor technical DD report | Yes | 46-56 | Developed design; permits; cost |
| ☐ | Prepare transaction documents and disclosure | Prepare SPA/asset sale structure, disclosure letter, warranties, limitations, assignment/novation schedule and closing conditions. | Transaction document suite | No | 52-62 | Vendor DD; buyer process |
| ☐ | Obtain RTB sign-off | Development lead, legal, technical, power and planning leads certify completion or clearly list accepted exceptions and cure plan. | Signed RTB certificate | Yes | 58-60 | All mandatory RTB items |

# 5. Buyer data room checklist

## Corporate

SPV constitutional documents

Shareholder register and ownership chart

Board/shareholder resolutions

Signing authorities and powers of attorney

Material litigation and compliance declarations

## Land

Option, purchase or lease agreements

Title report and cadastral documents

Boundary/topographical surveys

Easements, wayleaves and access rights

Geotechnical, contamination, flood and archaeology reports

## Power

Grid application and correspondence

Grid studies and capacity evidence

Binding connection offer

Executed connection agreement and payment evidence

Substation design, SLDs and utility programme

## Planning & Environment

Planning advice and authority minutes

Planning application and approved drawings

Final consent and conditions tracker

Building permit and fire approvals

Environmental studies and permits

## Technical

Masterplan and Basis of Design

Civil, structural, electrical and mechanical design

Security, controls and commissioning strategies

Independent technical review

Design assumptions and deviation register

## Fiber & Utilities

Carrier map and feasibility letters

Diverse route plans and wayleaves

Latency/resilience assessment

Water and utility capacity confirmations

Drainage and heat-reuse assessments

## Commercial

Market assessment

Customer/buyer target list

NDA and Q&A log

Tenant requirements, workshop minutes and LOIs

RTB sale materials

## Cost & Delivery

Development budget

Capital cost estimate

Contracting strategy

Contractor/supplier prequalification

Long-lead schedule, contractor proposals and integrated programme

## Financial, Tax & Insurance

Integrated financial model

Funding evidence

Tax structuring memorandum

Insurance strategy and indications

Development expenditure ledger

## Risk & ESG

Integrated risk register

Stakeholder plan

ESG strategy

Climate resilience assessment

HSE framework

## Transaction

RTB completion standard and signed certificate

Vendor legal and technical DD

Draft transaction documents

Disclosure and novation/assignment schedule

Data-room index and document register

# 6. Readiness scorecard

| Workstream | % | RTB | Status | Key blocker | Owner |
| --- | --- | --- | --- | --- | --- |
| Strategy & Development Definition | ___% | Yes | ________________ | ____________________________ | ________________ |
| Land & Site Control | ___% | Yes | ________________ | ____________________________ | ________________ |
| Power & Grid Connection | ___% | Yes | ________________ | ____________________________ | ________________ |
| Fiber & Telecommunications | ___% | Yes | ________________ | ____________________________ | ________________ |
| Planning, Environmental & Permitting | ___% | Yes | ________________ | ____________________________ | ________________ |
| Water, Cooling & Utilities | ___% | Yes | ________________ | ____________________________ | ________________ |
| Technical Design & Engineering | ___% | Yes | ________________ | ____________________________ | ________________ |
| Commercial: Tenant, Client & Exit | ___% | Yes | ________________ | ____________________________ | ________________ |
| Cost, Procurement & Delivery Strategy | ___% | Yes | ________________ | ____________________________ | ________________ |
| Financial, Tax, Insurance & Corporate | ___% | Yes | ________________ | ____________________________ | ________________ |
| Risk, ESG, HSE & Stakeholders | ___% | Yes | ________________ | ____________________________ | ________________ |
| RTB Transaction & Data Room | ___% | Yes | ________________ | ____________________________ | ________________ |

# 7. Final RTB gate

☐ Land controlled, title verified, and access/easements transferable

☐ Executed grid agreement with credible capacity, cost and delivery schedule

☐ Final planning consent and effective building permit

☐ Documented and deliverable diverse fiber solution

☐ Concept and developed design aligned with permits and grid

☐ Market-validated capex estimate, contracting strategy and construction programme

☐ Complete data room with vendor legal and technical DD

☐ Risk register with clearly disclosed residual exceptions

☐ RTB certificate signed by the relevant workstream leads